## Slide 1
CLL798D / CHL7903 · NETWORK SCIENCE · PRELIM REVIEW · 09 SEP 2026
Minimum spanning trees don't survive
contact with a hillside
Graph-theoretic topology optimisation of district-heating pipe networks — on two real German networks, real SRTM terrain, and a transport-phenomena cost model.
REAL NETWORKS
Bremen · Stuttgart
TERRAIN
NASA SRTM 30 m
ALGORITHMS
Kruskal · Prim · Steiner
Pathway 1 — reproduce and extend · Gao et al. (2020), Chem. Eng. Transactions 81, 277–282
Notes: TITLE - 15 s. One line: 'We asked whether the minimum spanning tree, which is the standard answer for pipe network layout, survives contact with real terrain. It does not, in three separate ways.' Then move straight on.

## Slide 2
02 SETUP · PROBLEM, DATA, METHOD
A pipe network is a graph, and the topology is the design decision
THE GRAPH
V = 1 plant + 40 substations
E = every feasible trench route
layout = spanning tree
candidates = 41^39 ≈ 10^62
REAL DEMAND
859 GWh/y
67,314 households, from the AixDHN census dataset
REAL TERRAIN
29,248 pts
NASA SRTM 30 m, sampled every 25 m along each route
RELIEF CONTRAST
63 m vs 282 m
Bremen against Stuttgart
Notes: SETUP - 45 s. Nodes are substations, edges are candidate trenches, a valid layout is a spanning tree, and there are 10^62 of them so you need an algorithm. Two REAL German networks from the AixDHN census dataset, real household demand, real SRTM terrain. Bremen is flat at 63 m relief, Stuttgart is 282 m. That contrast is the controlled experiment. Note the star on the left is 3x the pipe length. Move on quickly.

## Slide 3
03 RESULT 1 · TERRAIN-WEIGHTED ROUTING
A longer tree can be the cheaper tree
STUTTGART · HILLY
−3.0 % TAC
23.09 → 22.39 EUR/MWh, for a tree that is 0.03 km LONGER
BREMEN · FLAT
0.0 %
terrain weighting returns the identical tree — the control works
WHY IT MATTERS
Minimising length and minimising cost are the same problem only on flat ground. The saving is free — same algorithm, better edge weight.
Notes: RESULT 1 - 55 s. We replaced straight-line distance with terrain-weighted construction cost: 3D slope length times a trenching multiplier that rises with gradient, sampled on the real DEM. In Stuttgart this changes which tree is optimal and saves 3% of total annual cost - for a tree that is LONGER in metres. In flat Bremen it returns the identical tree, which is the control experiment behaving exactly as it must.

## Slide 4
04 RESULT 2 · HYDRAULIC FEASIBILITY
In Stuttgart the cost-optimal tree cannot legally be built
STATIC PRESSURE
p(z) = p₀ + ρg(z₀ − z)
ρgΔz over 282 m 26.3 bar
PN16 pipe class 16.0 bar
one-zone limit 151 m
PRESSURE ZONES NEEDED
Stuttgart 2 Bremen 1
an exchanger station breaks the static column
SPECTRAL BISECTION AT WORK
Where to split is a balanced minimum cut — separate by elevation, cut as few pipes as possible. The Fiedler vector of the Laplacian is the classical relaxation of exactly that.
Notes: RESULT 2 - 55 s. The binding terrain constraint is NOT pumping cost. In a closed supply/return loop the static head cancels - the return leg gives it back - so pumping is friction only. What does not cancel is the static pressure the pipe must physically hold: 282 m of relief is 26.3 bar against a PN16 pipe class. One zone can hold 151 m. So Stuttgart needs two pressure zones and Bremen needs one. We choose where to split with spectral bisection of the Laplacian - that is a balanced minimum cut, because every pipe crossing a boundary needs an exchanger station. Course material doing real engineering.

## Slide 5
05 RESULT 3 · RELIABILITY
Every tree edge is a bridge — and Steiner trees make it worse
STUTTGART · WORST SINGLE PIPE FAILURE
Star 43.72 40 br 95.6 %
MST-terrain 22.39 40 br 0.0 %
RSMT (cheapest) 20.87 59 br 0.0 %
MST-terrain +R 26.46 17 br 91.9 %
ANSWERING THE FAULT QUESTION
A Steiner tree is still a tree. It buys length — RSMT is the cheapest topology — but concentrates flow into shared trunks, so it is MORE fragile.
THE FIX COSTS 4.3 %
One redundant pipe: −57 % expected unserved demand, N−1 survival 0 → 68 %.
Notes: RESULT 3 - 60 s. Structurally, every edge of a tree is a bridge, so any single pipe failure strands everything downstream. This answers a question we were asked: does a Steiner tree fix it? No. A Steiner tree is still a tree. RSMT is the CHEAPEST topology we found at 20.87 EUR/MWh, but it has 59 bridges against the MST's 40, because Steiner points concentrate flow into shared trunks. Steiner solves cost; only cycles solve faults. Adding one redundant pipe costs 4.3% and removes 57% of expected unserved demand. Note the star is the most RELIABLE topology - that is the trade-off in one line.

## Slide 6
06 RESULT 4 · ALGORITHMS AND THE REPRODUCTION
Kruskal vs Prim, and two findings against the source paper
V = 1600, E = 1,279,200
Kruskal union-find 420 ms
Prim binary heap 6114 ms
Prim dense array 28.8 ms
WE WERE WRONG, AND MEASURED IT
We predicted density favours Prim. It favours DENSE Prim — 212× faster than the heap version. Kruskal wins by early exit, examining 0.7 % of edges.
PAPER FINDING 1
Table 2 is not self-consistent: the Star/MST cost ratio implies 357 kg/s, the absolute cost implies 87.5 — 3×.
PAPER FINDING 2
Reported ESMT/MST = 0.86555 sits below the proved Du–Hwang bound √3/2 = 0.86603.
Notes: RESULT 4 - 50 s. All three MST implementations written from scratch and verified to return identical tree weight. Our own earlier slides predicted that a dense graph favours Prim. The measurement says it favours the DENSE ARRAY Prim - 212x faster than the heap version - while heap Prim is the worst choice. Kruskal beats heap Prim by terminating early, examining 0.7% of the sorted edge list. On the reproduction: we matched the paper's MST column exactly, but found its Table 2 is not internally consistent, and its reported Steiner ratio sits below a proved geometric lower bound. If asked, we also re-derived their heat transfer coefficient independently to 0.16%.

## Slide 7
07 CONCLUSION
Terrain belongs in the weight. Pressure class belongs in the constraints. Reliability belongs in the objective.
COST
−3.0 %
terrain-weighted MST, Stuttgart
FEASIBILITY
2 zones
PN16 exceeded by 10 bar
RELIABILITY
+4.3 % → −57 %
cost premium vs unserved demand
ALGORITHMS
212×
dense Prim over heap Prim
On flat ground a minimum spanning tree is the right answer. On real terrain it is neither minimum-cost nor necessarily buildable — and because every tree edge is a bridge, it is never robust.
NEXT
Exact ILP bound on the greedy redundancy · seasonal part-load · a third district to test the 151 m threshold
DATA
AixDHN (RWTH Aachen, MIT) · NASA SRTM 30 m · EN 253 · Eurostat · Persson & Werner (2011)
Notes: CLOSE - 20 s. One sentence: terrain belongs in the edge weight, pressure class belongs in the constraints, reliability belongs in the objective. Then stop and take questions. Do NOT read the four numbers aloud - they are there for the audience to scan.